## Flow Measurement Specification

## F-3500 Insertion Magnetic Flow Meter

## For CEP CHW, HW and CW Applications  (20 – 60,000 ᶙS/cm)                        AUG 2013

# Flow Meter Specification

Provide an ONICON Model F-3500 Insertion Electromagnetic Flow Meter (or FB-3500 for Bi-directional flow applications), complete with all installation hardware necessary to enable insertion and removal of the meter without system shutdown. The flow meter shall be hand-insertable up to 400 psi. For installations in non-metallic pipe, install grounding rings or probes. Materials of construction for wetted metal components shall be 316 SS.  The flow meter shall average velocity readings from two sets of diametrically opposed electrodes.  Each flow meter shall be individually wet-calibrated against a primary volumetric standard that is accurate to within 0.1% and traceable to NIST*.  A certificate of calibration shall be provided with each flow meter. Accuracy shall be within ± 1% of rate from 2-20 ft/s. Overall turndown shall exceed 100:1.

Output signals shall be completely isolated and shall consist of the following: (1) analog output; 4-20mA, 0-10V, or 0-5V jumper selectable, (1) scalable dry contact output for totalization, and (1) high resolution frequency output for use with peripheral devices such as an ONICON display module or Btu meter.  FB-3500 for Bi-directional applications shall provide additional contact outputs for direction and flow totalization in each direction. Each flow meter shall be covered by the manufacturer’s two-year warranty.

# Optional Flow Display: D-100 Series Display Module for network interface and local / remote indication of flow rate and total.

Optional BTU Meter:  Provide an ONICON System-10 Series BTU meter. The BTU meter shall provide the following points both at the integral LCD and as outputs to the building control system: Energy Total, Energy Rate, Flow Rate, Supply Temperature and Return Temperature. Output signals shall be either serial network (protocol conforming to BACnet® MS/TP, BACnet/IP, LONWORKS®, JCI-N2, MODBUS RTU RS485, MODBUS RTU TCP/IP, or Siemens-P1) and/or via individual analog and pulse outputs.  The System-10 shall be provided with temperature sensors that are bath-calibrated and matched for the specific application, temperature thermowells and all required installation hardware. Each BTU meter shall be factory programmed for its specific application, and shall be re-programmable using the front panel keypad (no special interface device or computer required).

* National Institute of Standards and Technology